## Slide 1
COMMISSIONING & TESTING
Chilled-Water Flushing & Analysis
Project water-quality acceptance evidence
TECHNICAL
TECHNICAL TRAINING RESOURCE
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 2
COMMISSIONING & TESTING
Source to practice
Evidence, interpretation and technician application
02
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 3
KEY EVIDENCE
All six tested parameters were reported within control limits
10.54
pH (control 8.5-11.0)
2442
Conductivity, µS/cm (<3000)
1120
Nitrite as NaNO₂, ppm (800-1200)
TECHNICAL RESOURCE | Commissioning & Testing
03
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 4
TECHNICAL REVIEW
The sample supports initial chilled-water chemical control
• TDS was 1,619 ppm against a control limit below 2,100 ppm. • Total iron was 0.32 ppm against a control limit below 1.0 ppm.
• Suspended solids were reported as 6 ppm against a control limit below 30 ppm. • The laboratory conclusion states that all parameters were within control limits.
TECHNICAL RESOURCE | Commissioning & Testing
04
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 5
TECHNICAL REVIEW
A single compliant sample does not replace ongoing water management
• Confirm sampling point, flushing completion and sample date. • Trend pH, conductivity, TDS, iron, suspended solids and inhibitor concentration.
• Investigate makeup-water ingress, corrosion products and unexplained conductivity rise. • Retain laboratory reports with chemical dosing and flushing records.
TECHNICAL RESOURCE | Commissioning & Testing
05
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 6
SOURCE EVIDENCE
Water-analysis service report
CONTROLLED SOURCE
IDENTIFIERS REMOVED
Blutech Water FZC report 0116 - 21 April 2025
Use the current controlled document for detailed readings, revision status and formal acceptance.
TECHNICAL RESOURCE | Commissioning & Testing
06
Notes: [Sources]
- User-provided controlled technical document
- Evidence reference: Blutech Water FZC report 0116 - 21 April 2025
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 7
COMPETENCY CHECK
What technicians must retain
• Identify the correct controlled source before work. • Verify readings, configuration and acceptance criteria.
• Preserve evidence and escalate unresolved deviations. • Complete safe isolation, functional testing and handover records.
TECHNICAL RESOURCE | Commissioning & Testing
07
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.