## Slide 1
PROJECT HANDOVER
Project Chiller Handover Correspondence
Document closure, training, fan issue and spare-parts follow-up
TECHNICAL
TECHNICAL TRAINING RESOURCE
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 2
PROJECT HANDOVER
Source to practice
Evidence, interpretation and technician application
02
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 3
KEY EVIDENCE
The email chain shows repeated closure activity through 4 August 2025
4 Aug
Spare-parts document confirmed
15 days
Reported fan lead time
High
Multiple closure reminders
TECHNICAL RESOURCE | Project Handover
03
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 4
TECHNICAL REVIEW
Project closure depended on more than physical installation
• Training for remaining technicians was repeatedly requested. • Hard and soft copies of handover documents were requested.
• Warranty certificates, SOP and spare-parts information were identified as required. • Full cleaning and maintenance were linked to handover closure.
TECHNICAL RESOURCE | Project Handover
04
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 5
TECHNICAL REVIEW
Performance and alarm concerns delayed clean handover
• The Trane chiller was reported at 30% while an existing chiller was at 100% load. • An active alarm was reported again in July.
• Urgent attendance and corrective action were requested. • A cooling-fan supply lead time affected the handover timeline.
TECHNICAL RESOURCE | Project Handover
05
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 6
TECHNICAL REVIEW
Temporary file-transfer links created document-control risk
• Shared download links expired after three days. • IT restrictions prevented reliable download of some packages.
• Repeated resharing was required. • The final website library should use stable filenames and controlled updates.
TECHNICAL RESOURCE | Project Handover
06
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 7
TECHNICAL REVIEW
Parts identification was a specific handover requirement
• The initial shared information did not include sufficient part numbers. • A drawing showing the location of each part number was requested.
• This was considered essential for future ordering and identification. • The remaining spare-parts document was confirmed on 4 August 2025.
TECHNICAL RESOURCE | Project Handover
07
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 8
TECHNICAL REVIEW
The correspondence supports a formal closure checklist
• Training completion and attendance records • Final O&M manuals, SOPs and warranty certificates • Spare-parts list with physical location drawings
• Alarm/fan defect closure and performance verification • Signed handover and controlled-document register
TECHNICAL RESOURCE | Project Handover
08
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 9
COMPETENCY CHECK
What technicians must retain
• Identify the correct controlled source before work. • Verify readings, configuration and acceptance criteria.
• Preserve evidence and escalate unresolved deviations. • Complete safe isolation, functional testing and handover records.
TECHNICAL RESOURCE | Project Handover
09
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.