## Slide 1
COMMISSIONING & TESTING
Electrical Insulation Resistance Test
MTS and chiller feeder verification
TECHNICAL
TECHNICAL TRAINING RESOURCE
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 2
COMMISSIONING & TESTING
Source to practice
Evidence, interpretation and technician application
02
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 3
KEY EVIDENCE
All five tested circuits recorded 4,000 MΩ
5
Power circuits tested
800 A
Recorded MCCB rating
OK
Continuity result
TECHNICAL RESOURCE | Commissioning & Testing
03
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 4
TECHNICAL REVIEW
The test covered MTS interconnections and all three chiller feeders
• MTS 1 to MTS 3 and MTS 2 to MTS 3 were included. • MTS 3 to Chiller 03, MTS 1 to Chiller 01 and MTS 2 to Chiller 02 were included.
• R-Y, R-B, Y-B and RYB-N readings were recorded. • Cable and ECC sizes must remain linked to the approved single-line diagram.
TECHNICAL RESOURCE | Commissioning & Testing
04
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 5
TECHNICAL REVIEW
Acceptance requires more than a high resistance value
• Verify instrument calibration and test-voltage selection. • Confirm cables were disconnected from sensitive electronics before testing.
• Record ambient condition, circuit isolation and discharge after testing. • Retain signed results with termination torque and continuity evidence.
TECHNICAL RESOURCE | Commissioning & Testing
05
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 6
SOURCE EVIDENCE
Megger test schedule
CONTROLLED SOURCE
IDENTIFIERS REMOVED
TAB Engineering Services - Project roof-level circuits
Use the current controlled document for detailed readings, revision status and formal acceptance.
TECHNICAL RESOURCE | Commissioning & Testing
06
Notes: [Sources]
- User-provided controlled technical document
- Evidence reference: TAB Engineering Services - Project roof-level circuits
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 7
COMPETENCY CHECK
What technicians must retain
• Identify the correct controlled source before work. • Verify readings, configuration and acceptance criteria.
• Preserve evidence and escalate unresolved deviations. • Complete safe isolation, functional testing and handover records.
TECHNICAL RESOURCE | Commissioning & Testing
07
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.