## Slide 1
COMMISSIONING & TESTING
Chilled-Water Balancing Test
Chiller 03 flow verification
TECHNICAL
TECHNICAL TRAINING RESOURCE
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 2
COMMISSIONING & TESTING
Source to practice
Evidence, interpretation and technician application
02
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 3
KEY EVIDENCE
Measured flow achieved 101% of design
36.03
Design flow, L/s
36.62
Actual flow, L/s
12.03
Measured differential pressure, kPa
TECHNICAL RESOURCE | Commissioning & Testing
03
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 4
TECHNICAL REVIEW
The balancing valve was recorded fully open during testing
• Chiller 03 used a Crane DM931, 150 mm double-regulating valve. • The report records a design Kv value of 380.0.
• The reading was taken using a hydronic meter on 7 May 2025. • The stated operating condition was two pumps running with two chillers open.
TECHNICAL RESOURCE | Commissioning & Testing
04
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 5
TECHNICAL REVIEW
The operating condition must be reproduced when comparing future flow
• Confirm pump combination and chiller valve positions. • Verify strainers, air removal and differential-pressure sensor accuracy.
• Compare flow against current load, chilled-water temperature difference and pump speed. • Rebalance after material piping, valve or pump changes.
TECHNICAL RESOURCE | Commissioning & Testing
05
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 6
SOURCE EVIDENCE
Balancing-valve test report
CONTROLLED SOURCE
IDENTIFIERS REMOVED
Chiller 03 - 101% of design flow
Use the current controlled document for detailed readings, revision status and formal acceptance.
TECHNICAL RESOURCE | Commissioning & Testing
06
Notes: [Sources]
- User-provided controlled technical document
- Evidence reference: Chiller 03 - 101% of design flow
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.

## Slide 7
COMPETENCY CHECK
What technicians must retain
• Identify the correct controlled source before work. • Verify readings, configuration and acceptance criteria.
• Preserve evidence and escalate unresolved deviations. • Complete safe isolation, functional testing and handover records.
TECHNICAL RESOURCE | Commissioning & Testing
07
Notes: [Sources]
- User-provided controlled technical document
Training interpretation only. Verify against the current controlled record, OEM documentation, approved PTW/LOTO, risk assessment and site procedures.